## Sheet1
Recording
Functions
1.2.1(a) | Life recording of sensor/s data to a database;
1.2.1(b) | Exporting of selected sensor/s data to an external storage or program to assist in the analysis of the data;
Requirements
4.1 | Recording
4.1.1 | Facilities shall be provided by the Contractor to record the data from the Surveillance Monitoring Processor on a continuous basis without interruption i.e. 24 hours a day and 7 days a week. Data recordings shall be produced as specified and shall be sufficient for playback and offline analysis.
4.1.2 | The following types of recordings shall be provided: (a) Recent recordings available for immediate retrieval and played back using the technical display; (b) Archive recordings on low-cost removable media such as tapes/compact discs/DVD-Rs,
4.1.3 | The recording service shall at least be available to record the following: (a) Real-time Data from all sensors individually; (b) Performance graphs for all sensors individually;
4.1.4 | A quantity of removable volumes sufficient for archiving 60 days’ recordings in duplicate shall be delivered with the system.
4.1.5 | At least the most recent 48 hours’ recordings shall be available on sufficiently reliable bulk storage devices for the following purposes: (a) Facilitate immediate playback for urgent incident investigation (b) Provide sufficient time and data buffering for re-attempting archiving
4.1.6 | The Tenderer shall provide details which includes but not limited to the following: (a) How a recorder will be implemented? (b) Storage media, e.g. tape cartridges, compact discs, small removable drives, DVD-R, to be used for storing different types of recordings.
4.2 | Copying to Removable Media
4.2.1 | The recent recordings shall be copied to removable media as archive recordings automatically and not more frequently than once a month at an Adjustable System Parameter (ASP)-defined hour.
4.2.2 | It shall be possible to replicate a given set of recent recordings files on any number of removable media. The operator shall be alerted when more than an ASP-defined number of hours' recent recordings have not been copied out as archive recordings, e.g. because a blank tape cartridge/compact disc is not available.
4.2.3 | Every archive media shall have sufficient identification information. The media label/initialization file written by the recorder shall include identification, time/date, media number, archive period, etc. The detailed identification information shall be finalized with CAAS during implementation.
4.6 | Export of Data
4.6.1 | The Surveillance Monitoring Processor shall provide the facility to export the real time data stated in Para 4.1.3 to a standard database application.
4.6.2 | The exporting of data shall not affect the performance of the Surveillance Monitoring System.
4.6.3 | The database system shall allow the recorded information to be copied to CDR/ CD-RW/DVD discs. Tenderers shall also state the various methods to archive the recorded data.
Evaluation
Functions
1.2.1(d) | Generation and display of the performance of the selected sensor/s in the forms of graphs (For e.g. scattergraphs), diagrams (For e.g. horizontal and vertical polar diagrams, maps (For e.g. overlaying of the coverage diagram over the air situational picture) and reports(For e.g. in tabular format in excel sheet. The outputs for the above should also allow selection based on an user selectable field such as callsign.
Requirements
4.3 | Evaluation Facility
4.3.1 | Evaluation facility shall be provided based on the functions listed or provided by the Tenderers under Clause 1.2.1. The facility shall be used to evaluate the performance of the sensors by analyzing the input data from the sensors.
4.3.2 | Such facilities shall be made available for both the online monitoring and during playback of the sensor/s input data.
4.3.3 | The Evaluation Facility shall produce charts, diagrams, tables, etc as listed in Clause 1.2.1(d) after evaluation.
Statistics Generation & Play back
Functions
1.2.1(c) | Replaying of selected sensor/s data to the Technical Display, allowing overlay of the data from the database, without any interruption to the operations of the system;
Requirements
4.4 | Statistics Generation
4.4.1 | The Surveillance Monitoring System shall include the facilities to plot the footprint of targets based on the input from one or more sensors.
4.4.2 | The Surveillance Monitoring System shall include the facilities to generate the statistics on the number of targets detected within a definable geographical area for both surface and airborne targets. Such statistic shall include, but not limited to the following: a) Number of targets detected; b) Number of targets equipped with mode A/C transponders; c) Number of targets equipped with mode S transponders; d) Number of targets equipped with mode S extended squitters; e) Number of targets not equipped with transponders; f) Any other statistics to be listed.
4.4.3 | The Surveillance Monitoring System shall include the facilities to generate specific statistics on the targets detected within a definable geographical area. Such statistic shall include, but not limited to the following: a) Number of targets with the Navigation Uncertainty Category (NUC) above a certain definable value at more than a certain definable percentage of the time; b) Number of targets with less than a certain definable probability of detection from each sensor; c) Number of targets which display excessive accelaration (i.e. showing drastic velocity changes which may be caused by data inaccuracy); d) Number of targets with less than or more than a certain definable update rate; e) Any other statistics to be listed.
4.4.4 | The Surveillance Monitoring System shall include the facilities to generate other statistics on the targets detected within a definable geographical area. Such statistic shall include, but not limited to the following: a) Number of targets within various flight levels.
4.4.5 | The Surveillance Monitoring System shall include the facilities to generate the above statistics (para 4.4.1 to 4.4.4) using a filtered set of aircraft. This shall be based on, but not limited to, the 24-bit ICAO address. It may include other parameters which shall be defined by the Tenderer.
4.5 | Playback Facility
4.5.1 | The Air Situation Playback (APSB) Facility shall be provided at the Technical Display.
4.5.2 | The ASPB facility shall be designed for use by the equipment operator for investigative, analysis as well as for testing purposes.
4.5.3 | The ASPB facility shall be able to play back from any of the recordings types described in para. 4.1.2.
4.5.4 | The Tenderer shall describe the steps to be taken by the operator to make the recent recordings or replicates available to the ASPB facility.
4.5.5 | The ASPB facility shall allow the equipment operation to select the playback forward/backward at normal speed, fast forward/backward up to 10 times the actual speed as well as to freeze.
Status Monitoring And Remote Control
Alarm Alert System
Functions
1.2.1(e) | Real-time monitoring of sensor/s, providing both visual and audio alert when the sensor/s is not performing up to the user definable thresholds. This shall be based on, but not limited to, the following parameters (i) Coverage, (ii) Accuracy, (iii) Systematic Errors, (iv) Random Errors, (v) Probability of Detection, (vi) Probability of Mode A Code Detection, (vii) Probability of Mode C Code Detection, (viii) Resolution and (ix) Any other parameters shall be listed;
1.2.1(f) | Real-time display of selected sensor/s data, allowing overlaying of data, to a Technical Display. For e.g. radar tracks, MLAT and/or ADS-B reports, etc in Air Situational Display, coverage diagrams;
1.2.1(g) | Detection of the accuracy for each and every sensor, providing both visual and audio alert if it falls below the user definable thresholds. Tenderers shall advise on the alarms that will be generated and the type of threshold that users will be able to set for e.g. a value from 1 to 10;
1.2.1(h) | Derivation of probability of detection for each and every sensor, providing both visual and audio alert if any reduction of detection is detected based on user definable thresholds;
1.2.1(i) | Detection of coverage for each and every sensor, providing both visual and audio alert if any reduction of coverage is detected based on user definable thresholds;
1.2.1(j) | Determination of number of spurious (false) plots for each and every sensor, providing both visual and audio alert if the number exceeds the user definable thresholds;
1.2.1(k) | Detection of systematic / bias errors (i.e. slant range, azimuth, etc);
1.2.1(l) | Detection of random errors for each and every sensor, providing visual and audio alert if the number of occurrence exceeds a user definable value or thresholds;
1.2.1(m) | Detection of inconsistency in the reports between any 2 or more similar sensors (for e.g. between PSR, SSR and ADS-B reports, etc) and providing both visual and audio alert if any inconsistency is detected;
1.2.1(n) | Cross Detection of inconsistency in the reports between any 2 or more sensors sharing similar data (for e.g. between SSR mode C and ADS-B declared height, etc) and providing both visual and audio alert if any inconsistency is detected. Such alerts shall be based on a user definable value such as difference of more than 100ft for the above mentioned example;
1.2.1(o) | Detection of the resolution for each and every sensor, providing both visual and audio alert if the number exceeds the user definable thresholds; and
1.2.1(p) | Any other capability may be proposed.
Requirements
7.1 | System Alerts Notifications
7.1.1 | Alerts shall be send to the EFMS when any part of the Surveillance Monitoring System is down. This shall includes, but not limited to, the following; a. UPS is running on batteries, b. Either one or both Main Data Processor is not operating, c. Either one or both Input Interface is not operating, d. Either one or both Output Interface is not operating, e. When no data is detected for a user definable period from each and every individual sensor on either one or both ports of the Input Interface, f. Any other alerts shall be listed.
7.2 | Sensors Alerts Notifications
7.2.1 | Alerts shall be send to the EFMS when any sensor/s performance are detected to be dropping. This shall includes, but not limited to, the following; a. When any sensor coverage drops, b. When any sensor PD drops, c. When any sensor accuracy drops, d. When the systematic errors increases by 5% or a figure to be stipulated by the Tenderers, e. When the random errors occurs too frequently by a figure to be stipulated by the Tenderers, f. When any sensor resolution degraded, g. When the data between the two inputs from a single sensor appears to be different regularly, h. Any other alerts shall be listed.
Portable Monitoring Tool
Requirements
6.2 | Functionalities of the portable monitoring tool
6.2.1 | The Portable Monitoring Tool shall analyse the following when connected to a surveillance sensor. This shall include but not limited to; a) Analyse the surveillance coverage of the sensor; b) Analyse the probability of detection for the sensor; c) Analyse the accuracy of the sensor; d) Analyse the resolution of the sensor; e) Any other analysis functions to be listed.
6.2.2 | The Portable Monitoring Tool shall display the results of the various analyses via a user-friendly GUI.
6.2.3 | The Portable Monitoring Tool shall have the functionality to record the data from the sensor for at least 24 hours so that the recorded data can be used for further evaluation at the main Surveillance Monitoring System.